## Q3 2020-2021 All 2
GREATER TZANEEN MUNICIPALITY
WATER SERVICES LABORATORY
Tzaneen Cetral Laboratory
Portion 7 Dornhoek farm 535 LT
Tel:+27 15 307 8217/9
Fax :+27 15 307 8246
Ref no:ALL/ Q3/ 20-21/2/ January- March 2021
Area : Tzaneen, Nkowankowa, Letsitele and Haenertsburg
Date Sampled: Averaged: 3rd Quarter 2020/2021
Date analysed: Averaged Quartely
Determinants | Tzaneen | Nkowankowa | Letsitele | Haenertsburg | Standard limits
Ph (-logH) | 8.79 | 7.2 | 7.32 | 7.33 | > 5- ≤ 9.7 Operational
Turbidity (NTU) | 0.7 | 0.7 | 0.48 | 1.01 | ≤ 5 Aesthetic ≤ 1 Operational
Colour (as Pt) | 4.07 | 7.6 | 4.5 | 0.34 | ≤ 15 Aesthetic
Conductivity (mS/m) | 9.96 | 14.12 | 24.42 | 5.14 | ≤ 170 Aesthetic
Temperature 0C | 27.21 | 27.2 | 26.39 | 24.78 | N/A
Total Dissolved Solids (mg/l) | 47.17 | 66.63 | 143.17 | 24.42 | ≤ 1200 Aesthetic
Total Alkalinity (mg/l) | 34.38 | 42 | 81.14 | 21.67 | N/A
Total Hardness (mg/l) | 54.5 | 62 | 80.57 | 31 | N/A
Calcium Hardness as CaCO3 (mg/l) | 31.5 | 22 | 45.43 | 10.33 | N/A
Calcium as Ca (mg/l) | 12.61 | 8.8 | 18.19 | 4.13 | N/A
Magnesium Hardness as CaCO3 (mg/l) | 23 | 40 | 35.14 | 20.67 | N/A
Magnesium as Mg (mg/l) | 5.59 | 9.7 | 8.53 | 5.02 | N/A
Sodium as (Na) (mg/l) | 4.88 | 7.22 | 21.28 | 6.51 | ≤200 Aesthetic
Potassium as K (mg/l) | 0.38 | 12.32 | 1.17 | 0.93 | N/A
Chloride as Cl (mg/l) | 11.79 | 14.9 | 23.5 | 7.09 | ≤ 300 Aesthetic
Fluoride as F (mg/l ) | 0.41 | 0.3 | 0.09 | 0.04 | ≤ 1.5 Chronic Health
Sulphate as SO4 (mg/l) | 0.13 | 2 | 0 | 0 | ≤250 Aesthetic≤500 Acute Health-1
Nitrate as N (mg/) | 2.49 | 0.6 | 0.01 | 1.1 | ≤ 11 Acute health-1
Iron as Fe (µg/l) | 6.25 | 141.6 | 14 | 41.67 | ≤300Aesthetic ≤2000 Chronic Health
Manganese as Mn (µg/l) | 31 | 0 | 8.29 | 33.33 | ≤100 Aesthetic ≤ 400 Chronic Health
Ammonia as N (mg/l) | 0 | 0.38 | 0 | 0 | ≤ 1.5 Aesthetic
Aluminium as Al (µg/l) | 81.25 | 83.4 | 15.57 | 29.67 | ≤300 Operational
Zinc as Zn (mg/l) | 0.79 | 0.22 | 0.33 | 1.48 | ≤ 5 Aesthetic
Langelier Sat. Index | 0.2 | -1.3 | -1.64 | -1.81 | N/A
Ryznar Index | 8.19 | 9.78 | 8.44 | 11.01 | N/A
Corrosivity Ratio | 0.41 | 0.28 | 0.42 | 0.49 | N/A
Free Res. Chlorine (mg/l) | 0.15 | 0.15 | 0.13 | 0.27 | ≤ 5 Chronic Health
E.Coli (count/100ml) | 0 | 0 | 0 | 0 | 0 Acute Health-1
Total Coliform Bacteria(count/100ml) | 0 | 0.8 | 0.5 | 0 | ≤10 Operational
= Outside limit
Signature : ………………………………………………………………… |  |  | Date : ……………………………………………………