## Q2 2020-2021 All 3
GREATER TZANEEN MUNICIPALITY
WATER SERVICES LABORATORY
Tzaneen Cetral Laboratory
Portion 7 Dornhoek farm 535 LT
Tel:+27 15 307 8217/9
Fax :+27 15 307 8246
Ref no:ALL/ Q2/ 20-21/3/ October-December 2020
Area : Tzaneen, Nkowankowa, Letsitele and Haenertsburg
Date Sampled: Averaged: 2nd Quarter 2020/2021
Date analysed: Averaged Quartely
Determinants | Tzaneen | Nkowankowa | Letsitele | Haenertsburg | Standard limits
Ph (-logH) | 8.5 | 8.26 | 7.95 | 9.5 | > 5- ≤ 9.7 Operational
Turbidity (NTU) | 0.67 | 0.69 | 0.34 | 0.51 | ≤ 5 Aesthetic ≤ 1 Operational
Colour (as Pt) | 5.34 | 6.6 | 4.14 | 4 | ≤ 15 Aesthetic
Conductivity (mS/m) | 8.83 | 17.01 | 23.38 | 5.71 | ≤ 170 Aesthetic
Temperature 0C | 25.27 | 27.09 | 25.16 | 20.93 | N/A
Total Dissolved Solids (mg/l) | 46.26 | 66.31 | 140.16 | 31.64 | ≤ 1200 Aesthetic
Total Alkalinity (mg/l) | 31.25 | 41 | 67.86 | 20 | N/A
Total Hardness (mg/l) | 45.63 | 47 | 75.71 | 40 | N/A
Calcium Hardness as CaCO3 (mg/l) | 26.25 | 26 | 39.29 | 15 | N/A
Calcium as Ca (mg/l) | 10.51 | 10.4 | 15.73 | 6.01 | N/A
Magnesium Hardness as CaCO3 (mg/l) | 19.38 | 21 | 36.43 | 25 | N/A
Magnesium as Mg (mg/l) | 4.71 | 5.12 | 8.84 | 6.07 | N/A
Sodium as (Na) (mg/l) | 5.07 | 9.18 | 23.21 | 5.86 | ≤200 Aesthetic
Potassium as K (mg/l) | 1.68 | 12.32 | 1.57 | 0.9 | N/A
Chloride as Cl (mg/l) | 10.81 | 20.58 | 25.83 | 10.64 | ≤ 300 Aesthetic
Fluoride as F (mg/l ) | 0.27 | 0.5 | 0.11 | 0.43 | ≤ 1.5 Chronic Health
Sulphate as SO4 (mg/l) | 0.5 | 1.2 | 3.43 | 0 | ≤250 Aesthetic≤500 Acute Health-1
Nitrate as N (mg/) | 0.04 | 0.86 | 1.26 | 0.09 | ≤ 11 Acute health-1
Iron as Fe (µg/l) | 70.13 | 46.8 | 20 | 55 | ≤300Aesthetic ≤2000 Chronic Health
Manganese as Mn (µg/l) | 64.29 | 7.6 | 8.57 | 0.5 | ≤100 Aesthetic ≤ 400 Chronic Health
Ammonia as N (mg/l) | 0.05 | 0 | 0.02 | 0.09 | ≤ 1.5 Aesthetic
Aluminium as Al (µg/l) | 107.75 | 13.4 | 30.43 | 53 | ≤300 Operational
Zinc as Zn (mg/l) | 0.09 | 0.32 | 0.29 | 0.27 | ≤ 5 Aesthetic
Langelier Sat. Index | -0.1 | -0.16 | -1.2 | 0.14 | N/A
Ryznar Index | 8.72 | 8.64 | 8.63 | 9.13 | N/A
Corrosivity Ratio | 0.42 | 0.32 | 0.59 | 0.75 | N/A
Free Res. Chlorine (mg/l) | 0.17 | 0.18 | 0.12 | 0.24 | ≤ 5 Chronic Health
E.Coli (count/100ml) | 0 | 0 | 0 | 0 | 0 Acute Health-1
Total Coliform Bacteria(count/100ml) | 0 | 1.6 | 0.57 | 0 | ≤10 Operational
= Outside limit
Signature : ………………………………………………………………… |  |  | Date : ……………………………………………………